University of Virginia Energized Electrical Work Permit (Revised 10/’13)

FILLOUT Pages (1) through (3)

***Return completed and approved form to Safety Department for recordkeeping.*** Fax: 982-5894; Messenger Mail: Box 400726

| SECTION I |  |  |  |  |  | Work Order # |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Extended Duration: | One time use only |  |  |  | Date Start: |  |  |  |  |  | Expiration Date: |
| Building: |  |  | Room/Area: |  |  |  |  |  | Job Supervisor: |  |  |
| Description of work to be done: |  |  |  |  |  |  |  |  |  |  |  |
| Description of Circuit/Equipment: |  |  |  |  |  |  |  |  |  |  |  |
| Justification for why equipment cannot be de-energized: |  |  |  |  |  |  |  |  |  |  |  |
| SECTION II Approvals to perform the work while electrically energized |  |  |  |  |  |  |  |  |  |  |  |
| (Add signature and date) |  |  |  |  |  |  |  |  |  |  |  |
| Supervisor |  |  |  |  |  |  | Superintendent |  |  |  |  |
| Qualified Worker |  |  |  |  |  |  | Qualified Worker |  |  |  |  |
| Other - list name(s) and work title(s) |  |  |  |  |  |  |  |  |  |  |  |
| (Signature of Qualified Worker verifies the worker is trained and informed of all hazards relevant to this work task). |  |  |  |  |  |  |  |  |  |  |  |
| SECTION III Shock Hazard Analysis Results |  |  |  |  |  |  |  |  |  |  |  |
| NFPA 70E 2012 – Table 130.4(C)(a), page (24)- Protective Boundaries and Class rating for insulating equipment and tools |  |  |  |  |  |  |  |  |  |  |  |
| Shock Hazard Maximum Voltage |  |  |  | Glove Voltage Rating (Inspect gloves before use and check certification date.) |  |  |  |  |  |  |  |
| Limited Approach Boundary ft. (Recommend to use 10 ft. rule) |  | Restricted Approach Boundary ft. |  |  |  |  |  |  |  | Prohibited Approach Boundary ft. |  |
| SECTION IV Flash Hazard Analysis Results |  |  |  |  |  |  |  |  |  |  |  |
| NFPA 70E 2012 – Table 130.7 (C)(15)(a) pages (33-38)- Hazard Rating & Protective Boundaries |  |  |  |  |  |  |  |  |  |  |  |
| Flash Hazard Risk Categories Circle – 0, 1, 2, 3, 4 |  |  |  |  |  |  |  | Flash Protection Boundary ft. |  |  |  |
| 70E-2012 doesn’t defer to 4 ft. as a default arc flash boundary-[Refer to section 130.5(A) Arc Flash Boundary-(26)] A 4ft. default boundary is a minimum conservative safety distance. Maintain this distance for “other workers” who may be involved in the work (i.e. – to observe or relay information) but will not directly perform or assist in the work-(Voltages >50V-<600V)]. See Annex H.4 Notes (page 86) for further information on acceptable Flash Protection Boundaries.- |  |  |  |  |  |  |  |  |  |  |  |
| ATTENTION – See NOTES (1)-(6) at end of Table 130.7 (C)(15)(a) for short circuit current capacities and fault clearing times. Contact the FM Safety Manager if you need additional assistance for the system you will be working on (i.e. - clearance time of the interrupting device, age or integrity of the system, or the work task is not clearly defined in the Table). He will coordinate services with the Electrical Engineer. |  |  |  |  |  |  |  |  |  |  |  |
| NFPA 70E 2012 – Table 130.7(C)(16) - pages (39-40) Protective Clothing *Wear cotton underwear (conventional tee shirt& brief shorts) underneath arc rated PPE. |  |  |  |  |  |  |  |  |  |  |  |
| Hazard Risk Category 0 – Lowest Risk (Minimum Arc Rating PPE) Required: 100% cotton work clothing (long sleeve shirt and pants), safety glasses, leather shoes, and hearing protection (ear canal inserts). May be required: Leather gloves as needed. See Note (1) Table1307(C)(16)-page 40. *Special Note: Work tasks with Incident Energy levels equal to 1.2 cal per cm2 will require Hazard Category 1 protective clothing. |  |  |  |  |  |  |  |  |  |  |  |
| Hazard Risk Category 1 – Low Risk. Minimum Arc Rating PPE-4 cal/cm2 |  |  |  |  |  |  |  |  |  |  |  |
| Required: Base underneath-100% cotton work clothing (long sleeve shirt and pants); safety glasses, leather shoes, hearing protection (ear canal inserts), Class *G or *E hard hat and heavy duty leather gloves as needed. See note (1) in Table (if voltage rated gloves are required the leather protectors meet this requirement). Required: {AND} Arc rated face shield or arc flash suit hood {AND} coverall (i.e. Indura Westex ® Arc Rating 11 cal per cm2 ) {or} Nomex® Ltd ) {or} FR pants and FR long sleeve shirt *Hard Hat Electrical Classes: G (General) proof tested to 2200 volts; E (Electrical) proof tested to 20, 000 volts. |  |  |  |  |  |  |  |  |  |  |  |
| Hazard Risk Category 2 – Medium Risk Minimum Arc Rating PPE-8 cal/cm2 |  |  |  |  |  |  |  |  |  |  |  |
| Required: Base underneath- 100% cotton work clothing (long sleeve shirt and pants); safety glasses, leather shoes, hearing protection (ear canal inserts), Class G or E hard hat and heavy duty leather gloves. See Note (1) in Table (if voltage rated gloves are required the leather protectors meet this requirement). Required: {AND} coverall (i.e. Indura Westex ® Arc Rating 11 cal/cm2) {AND} arc flash suit hood or; Arc rated face shield and arc rated balaclava – Face shield must have wrap around guarding to protect not only the face but forehead, ears and neck. |  |  |  |  |  |  |  |  |  |  |  |
| Hazard Risk Category 3 – High Risk Minimum Arc Rating PPE-25 cal/cm2 |  |  |  |  |  |  |  |  |  |  |  |
| Required: Base underneath- 100% cotton work clothing (long sleeve shirt and pants); safety glasses, leather shoes, hearing protection (ear canal inserts) and Class G or E hard hat. Required: {AND} FR jacket and pants – Indura Westex ® Arc Rating 45 cal/cm2 {AND} Flash suit hood {AND} Arc rated gloves |  |  |  |  |  |  |  |  |  |  |  |
| Hazard Risk Category 4 VERY HIGH RISK! Minimum Arc Rating PPE-40 cal/cm2 STOP! THINK! RE-EVALUATE FEASIBILITY OF SHUTDOWN. |  |  |  |  |  |  |  |  |  |  |  |
| * SPECIAL NOTE: Consultation strongly recommended determining additional layering of FR clothing to achieve higher calorie/cm2. Required: Base underneath- 100% cotton work clothing (long sleeve shirt and pants); safety glasses, leather shoes, hearing protection (ear canal inserts), Class G or E hard hat. Required: {AND} FR jacket and pants – Indura Westex ® Arc Rating 45 cal/cm2 required. {AND} Flash suit hood required. {AND} Arc rated gloves |  |  |  |  |  |  |  |  |  |  |  |
| Section V |  |  |  |  |  |  |  |  |  |  |  |
| Document Safety Checklist |  |  |  |  |  |  |  |  |  |  |  |
| Remove all jewelry and metal apparel (i.e. – belt buckles) Insulated tools and equipment required. |  |  |  |  |  |  |  |  |  |  |  |
| All workers, including attendant, must be trained, qualified and have full knowledge of equipment. |  |  |  |  |  |  |  |  |  |  |  |
| Use Buddy System. Attendant worker must be able to cut off all power sources in the event of an emergency and have emergency communication equipment (i.e. – radio, cell phone). |  |  |  |  |  |  |  |  |  |  |  |
| Use barricade and warning signs. |  |  |  |  |  |  |  |  |  |  |  |
| Document Job debriefing including discussion of any job specific hazards – [Reference: NFPA70E 2012-Annex I, (Page 88) is one resource and is included as page (3) in the Permit.] |  |  |  |  |  |  |  |  |  |  |  |
| Check here if any additional information is added to this work permit such as special requirements, procedures or written work plans. |  |  |  |  |  |  |  |  |  |  |  |

Page 2

|  | Section VI - Job Debriefing |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Document job debriefing when energized work is performed and keep with the Energized Electrical Work Permit. |  |  |  |  |
| Identify |  |  |  |  |  |
|  |  |  | The hazards |  | Any unusual work conditions |
|  |  |  | The voltage levels involved |  | Number of people needed to do the job |
|  |  |  | Skills required |  | The shock protection boundaries |
|  |  |  | Any “foreign” (secondary source) |  | The available incident energy |
| Ask |  |  |  |  |  |
|  |  |  | Are backfeeds of the circuits to be worked on possible? |  | Is a “standby person” required? |
| Check |  |  |  |  |  |
|  |  |  | Job plans |  | Safety procedures |
|  |  |  | Single-line diagrams and vendor prints |  | Vendor information |
|  |  |  | Status board |  | Individuals are familiar with the facility |
|  |  |  | Information on plant and vendor resources is up to date |  |  |
| Know |  |  |  |  |  |
|  |  |  | What the job is? |  | Who is in charge? |
|  |  |  | Who else needs to know—Communicate! |  |  |
| Think |  |  |  |  |  |
|  |  |  | About the unexpected event…What if? |  | Install and remove grounds |
|  |  |  | Lock - Tag - Test - Try |  | Install barriers and barricades |
|  |  |  | Test for voltage - FIRST |  | What else…? |
|  |  |  | Use the right tools and equipment, including PPE |  |  |
| Prepare for an emergency |  |  |  |  |  |
|  |  |  | Is the standby person CPR trained? |  | What is the exact work location? |
|  |  |  | Is the required emergency equipment available? Where is it? |  | How is the equipment shut off in an emergency? |
|  |  |  | Where is the nearest telephone? |  | Are the emergency telephone numbers known? |
|  |  |  | Where is the fire alarm? |  | Where is the fire extinguisher? |
|  |  |  | Is confined rescue available? |  | Are radio communications available? |

Page 3